| USER’S MANUAL 192321782001006 Charger 1000W |  |  |
| --- | --- | --- |
| Appendix |  |  |
| CAUTION: Input and output end wiring of charger please really lock on endson, avoid equipment got burned by contact impendence. |  |  |
| Placement of the Unit |  |  |
| Set up |  |  |
| - Tower: Connect Utility and DC Plug |  | - RT: Connect Utility and DC Plug |

Parallel Connection

◎Number of parallel unit is up to 4. ----- When connect 2 groups of Charger 1000W in parallel , please select UL 1015 16AWG line material or the equal line material for the charger line in parallel of input and output -----When connect 3 or 4 groups of Charger 1000W in parallel , please select UL 1015 14AWG line material or the equal line material for the charger line in parallel of input and output

Specifications

AC INPUT. Input Voltage; 160V-280V. Current; 4.6Arms Max.. Freq.; 50Hz/60Hz±10%. Power Factor; ＞0.85. DC OUTPUT. Output Voltage; # 273Vdc ± 3Vdc (NO LOAD). DC Output Current; 5.0A Max.. Power Capacity; 1000W Max.. Efficiency; ＞0.85 at full load. Power Up Time; ＜75ms. Line Regulation; ≦1%(No LOAD). Ripple; Approximate ±5V. Noise; Approximate ±3V. ENVIRONMENTAL. Operation Temperature; 0℃ ~ 40℃. Cooling; Forced air ventilation by DC fan.. Humidity; 10% ~ 90% RH. PHYSICAL. Dimensions (WxLxH)mm; 166.0 x 282.0 x 86.0. Net Weight (Kgs); 3.2. PS：Most greatly may parallel to 4000W ( the maximum input current: 18.4A， maximum charging current: 20.0A)